## Sheet1
Identifier | Face image | Long Description | Height Range | Width Range | Wall or Ceiling or Both (Dual) | Fire Rating | Fire Test Standard | Fire Performance Rating | Fire Tested Side | Fire Tested Size H x W mm | Assessed Maximum Panel Sizes | Size range: Minimum to maximum (H × W mm). Fire Rated Panels: See assessed maximum panel sizes for allowable increases. | Smoke Test Standard | Air Permeability Test Standard | Air Permeability Rating | Acoustic Test Standard | Acoustic Rating | Corrosion class C1, C2, C3, C4 | Ceiling Types | Structural Opening Size | Panel Size Formula H x Wmm | Clear opening size through the installed panel with the door leaf open at 90 degrees | Quality Category | Product Design Category | Ironmongery Details | Lock Security Level | Frame Architrave Width (e.g. Picture / Beaded Frame) | Frame Steel Thickness | Door Steel Thickness | Door & Frame Material Grade | Frame Depth | Board Infill Type | Door Insulation Type | Seal Type | Paint Type
R51/120S/MD/PF/L12A/ATN/40A | https://images.onetimepim.com/acc-174/images/51-120s-md-pf-3wl-atn-40db_face_kvqljr.jpg?twic=v1/inside=300x300 | Premium Riser Door, Supplied with a Spring Pin Hinge System, 1.2mm Thick Door Leaf, 1.5mm Thick Frame, 2 Hour fire rated & Ambient Smoke Control Tested, Metal Door, 25mm wide Picture Frame, 3 Point Locking System, Single Door Unit, Airtight Panel, 40 dB Acoustic Rated, Powder Coated RAL 9010 30% Gloss. | 300 - 2,400 mm | 300 - 900 mm | Wall | 2 Hour Fire Rated | BS EN 1634-1: 2014+A1:2018 | Integrity (E) | Wall application Both Sides (Bidirectional / opening in either direction with respect to the fire risk side) | 2400x900mm | Up to 15% increase in height, 15% width and up to 20% area. | 1797x448mm up to 2400x900mm | BS EN 1634-3: 2004 | BS EN 1026: 2016 | 600Pa CLASS 2 | BS EN ISO 10140-2: 2010 | 40dB | C1 - Very Low: Exterior: Not suitable for outdoor use. Interior: Heated buildings with clean atmospheres, e.g. offices, shops, schools, hotels. | Not Suitable for a Ceiling Application | Panel Height Size + 10mm x Panel Width Size + 10mm | Inside Frame Size | Panel Height - 50mm x Panel Width - 100mm | Premium Range | Standard Product | 3 Point Locking System. Bright Zinc Plated Mild Steel,Fast Fit Spring Pin Pivot Hinge manufactured from electroplated steel | Grade 1 – Low Security | 25mm | 1.5mm | 1.2mm | Frame: Zintec Steel to BS EN 10152 : 2017 DC01 + ZE 25/25,Door Leaf: Zintec Steel to BS EN 10152 : 2017 DC01 + ZE 25/25 | 78mm | 12.5mm Thick GTEC dB Board | 5mm Thick IsoBase R50 ,40mm Thick Rockwool RW3 | 9mm x 5.5mm White 'P' Profile Compression Self Adhesive Neoprene Seal,Envirograph G10/10 10mm x 2mm Self Adhesive Intumescent Strip,Sealed to All Door Closing Edges | Polyester Powder Coated,RAL 9010 30% Gloss Pure white