## Sheet1
Identifier | Face image | Long Description | Height Range | Width Range | Wall or Ceiling or Both (Dual) | Fire Test Standard | Fire Performance Rating | Fire Tested Side | Fire Tested Size H x W mm | Assessed Maximum Panel Sizes | Size range: Minimum to maximum (H × W mm). Fire Rated Panels: See assessed maximum panel sizes for allowable increases. | Smoke Test Standard | Airtightness Tested | Acoustic Tested | Corrosion class C1, C2, C3, C4 | Ceiling Types | Structural Opening Size | Panel Size Formula H x Wmm | Clear opening size through the installed panel with the door leaf open at 90 degrees | Quality Category | Product Design Category | Lock Security Level | Frame Architrave Width (e.g. Picture / Beaded Frame) | Frame Steel Thickness | Door Steel Thickness | Door & Frame Material Grade | Frame Depth | Board Infill Type | Door Insulation Type | Seal Type | Paint Type
R16/120S/MD/PF/L11A/L33A/IP43/FPC | https://images.onetimepim.com/acc-174/images/16-120s-md-pf-bl-8tri_face_d5cljt.png?twic=v1/inside=300x300 | Metal Faced Meter Box, 2 Hour fire rated & Ambient Smoke Control Tested, Metal Door, 25mm wide Picture Frame, Budget Lock, 8mm Triangular Electrical Cabinet Insert, Single Door Unit, Ingress Protection Rating of IP43, Powder Coated RAL 9010 30% Gloss, Fully Powder Coated. | 300 - 1,070 mm | 200 - 650 mm | Wall | BS EN 1363-1: 2012,BS EN 1634-1: 2014+A1:2018 | Integrity (E) | Wall application Rear (Services side / opening away from the fire risk side) | 1070x650mm | Up to 15% increase in height, 15% width and up to 20% area. | 300x200mm up to 1070x650mm | BS EN 1634-3: 2004 | No Rating | No Rating | C2 - Low: Exterior: Low-pollution rural environments. Interior: Unheated buildings prone to condensation, e.g. depots and sports halls. | Not Suitable for a Ceiling Application | Wall Structural Opening or Existing Overall Meter Box Size Height & Width | Structural Opening or Existing Overall Meter Box Size +5mm | Panel Height - 0mm x Panel Width - 30mm | Mid Range | Standard Product | Grade 2 – Standard Security | 25mm | 1.2mm | 0.9mm | Frame: Zintec Steel to BS EN 10152 : 2017 DC01 + ZE 25/25,Door Leaf: Zintec Steel to BS EN 10152 : 2017 DC01 + ZE 25/25 | 70mm | None | None | Norseal FS1000 Self Adhesive Intumescent Foam Tape ,Sealed to All Door Closing Edges | Polyester Powder Coated,RAL 9010 30% Gloss Pure white